## Slide 1: GEOTECHNICAL CHALLENGES: I-40/I-240 INTERCHANGE PHASE II
Presented by
Ashraf S. Elsayed, Ph.D., P.E., D.GE
STGEC Annual Meeting
Biloxi, MS
November 8, 2016

## Slide 2: OUTLINE
Project Overview
Pile dynamics
Seismic issues
Retaining walls
Q’s

## Slide 3: I-40/I-240 EAST INTERCHANGE

## Slide 4: PROJECT SUMMARY
Busiest intersection in TN (more than 200,000 vehicles currently, over 350,000 vehicles by 2035)
Largest project contract awarded by TDOT (~$110M) at the time
Design is accordance with 2012 AASHTO LRFD
Six bridges: 2 new direct flyovers, Improvement of 4 existing bridges
23 retaining walls
Noise walls
More than 100,000 feet of piles
Construction period: 42 months

## Slide 5: GEOTECHNICAL SUBSURFACE EXPLORATION
Started in 1999
Completed in 2013
  340 SPT borings
  Conventional sampling & testing
  Supplemental Cone Penetration Testing (CPT)
Two site-specific seismic studies

## Slide 6: GENERAL SUBSURFACE CONDITIONS

## Slide 7: SITE-SPECIFIC SEISMIC STUDY

## Slide 8: BENEFIT OF SITE-SPECIFIC STUDY
I-40/I-240 Interchange Bridge1, Memphis, TN
Pile Tip El. 215.5
Pile Tip El. 209.5

## Slide 9: PILE DYNAMICS
Pile resistance has been typically evaluated by performing static load tests
Installation blow counts of driven piles have been used as a QC tool
The Engineering News (EN) formula has been used to assess the capacity (FoS = 6.0)
TDOT decided to allow high-strain dynamic testing of piles as the sole method of resistance evaluation

## Slide 10: PILE DYNAMICS cont.
A resistance factor of 0.65 in the design (dynamic testing of at least two production piles per site condition, but no less than 2% of the production piles)
Testing was performed on production piles during initial driving and 7-day restrike
The nominal axial resistances were then estimated using the CAse Pile Wave Analysis Program (CAPWAP)

## Slide 11: TEST PILE INSTALLATION SUMMARY
Test No. | Bridge No. | Bent No. | Pile No. | Embed. (ft.) | Average of Bottom 5 feet |  | Average of Bottom One foot | 
 |  |  |  |  | Stroke (ft.) | Blow Count (blows/ft.) | Stroke (ft.) | Blow Count (blows/ft.)
1 | 1 | 3 | 71 | 29.0 | 7.60 | 60 | 8.50 | 64
2 |  | 5 |  | 37.0 | 7.80 | 112 | 7.80 | 117
3 |  | 7 | 64 | 28.0 | 7.70 | 69 | 7.60 | 75
4 |  | RW17 | 8 | 45.0 | 7.90 | 83 | 8.00 | 70
5 | 2 | RW19 | 23 | 49.0 | 7.70 | 74 | 7.70 | 79
6 |  | 2 | 1 | 34.0 | 7.80 | 87 | 8.00 | 98
7 |  | 4 | 1 | 19.0 | 7.50 | 116 | 7.80 | 118
8 |  | 5 | 64 | 23.0 | 8.70 | 53 | 9.00 | 52
9 |  | 7 | 64 | 37.0 | 9.00 | 59 | 9.00 | 62
10 |  | 9 | 1 | 30.0 | 7.90 | 141 | 8.30 | 117
11 |  | 11 | 72 | 30.0 | 5.90 | 67 | 6.60 | 150
12 |  | 12 | 8 | 14.5 | 6.60 | 33 | 7.10 | 41
13 |  | Abut. 2 | 1 | 31.0 | 5.60 | 155 | 5.70 | 201
14 | 4 | RW12 | 1 | 18.0 | 7.50 | 50 | 7.70 | 60

## Slide 12: SUMMARY OF TEST RESULTS
Test No. | Static Resistance (kip) | End-of-Drive CAPWAP Resistance (kip) | Restrike Age (Days) | Restrike CAPWAP Resistance (kip) |  | 
 |  |  |  | Total | Side | Tip
1 | 371 | 290 | 7 | 337 | 303 | 34
2 | 612 | 409 | 8 | 545 | 521 | 24
3 | 420 | 393 | 7 | 399 | 297 | 102
4 | 826 | 335 | 7 | 788 | 742 | 46
5 | 660 | 306 | 7 | 630 | 574 | 56
6 | 410 | 330 | 8 | 345 | 219 | 126
7 | 400 | 379 | 7 | 393 | 100 | 293
8 | 425 | 397 | 7 | 415 | 226 | 189
9 | 328 | 258 | 7 | 274 | 196 | 78
10 | 450 | 397 | 7 | 439 | 93 | 346
11 | 400 | 327 | 7 | 344 | 277 | 67
12 | 238 | 222 | 5 | 227 | 78 | 149
13 | 304 | 253 | 7 | 272 | 64 | 208
14 | 403 | 305 | 7 | 356 | 117 | 239

## Slide 13: OBJECTIVES
Can pile setup in western Tennessee be estimated with an acceptable accuracy?
Can one or more of the available pile driving formulae (i.e., dynamic formulae) be used to predict the long-term nominal axial resistance indicated by the dynamic testing results?
How should the terminal driving resistance be used for quality control?
Can we detect pile damage due to overstressing during driving?

## Slide 14: ESTIMATING SETUP
Modified Bogard & Matlock (B‑M) equation:
Q(t): the resistance at time t,
Qu: the nominal resistance with 100% of setup realized
T50: the time required to realize 50% of pile setup
a: empirical coefficient in the range of 0.2 to 0.5

## Slide 15: SITE CORRELATION
T50 was estimated to be 0.5 to 2 days, based on site conditions (low-plasticity clays, silts and sands)
An a value of 0.2 appears to be suitable when tip resistance is less than 40 percent of the total resistance
When tip resistance is more than 40 percent of the total resistance, an a value of 0.5 appears to be suitable

## Slide 16: RESULTS
Bridge 1 Bent 3 (Test 1) a = 0.2 & 0.5
Chart: Square Root of Time, Days
| 2.6457513110645907
CAPWAP | 1498.976
 | 1289.92
T50=2 Days α=0.2 | 770.0971 | 990.1248 | 1356.8377 | 1485.1872 | 1567.6976 | 1628.5659
T50=1 Day α=0.2 | 990.1248 | 1210.1525 | 1485.1872 | 1562.1969 | 1607.622 | 1639.2975
T50=1/2 Day α=0.2 | 1210.1525 | 1386.1747 | 1562.1969 | 1604.685 | 1628.5659 | 1644.7301
T50=2 Days α=0.5 | 1100.1387 | 1237.656 | 1466.8516 | 1547.07 | 1598.639 | 1636.6817
T50=1 Day α=0.5 | 1237.656 | 1375.1733 | 1547.07 | 1595.2011 | 1623.5917 | 1643.389
T50=1/2 Day α=0.5 | 1375.1733 | 1485.1872 | 1595.2011 | 1621.7561 | 1636.6817 | 1646.7843

## Slide 17: RESULTS cont.
Bridge 2 Abutment 2 (Test 13) a = 0.2 & 0.5
Chart: Square Root of Time, Days
| 2.6457513110645907
 | 1209.856
 | 1125.344
T50=2 Days α=0.2 | 631.0229 | 811.3152 | 1111.8023 | 1216.9728 | 1284.5824 | 1334.4583
T50=1 Day α=0.2 | 811.3152 | 991.6075 | 1216.9728 | 1280.0751 | 1317.2967 | 1343.2519
T50=1/2 Day α=0.2 | 991.6075 | 1135.8413 | 1280.0751 | 1314.8902 | 1334.4583 | 1347.7034
T50=2 Days α=0.5 | 901.4613 | 1014.144 | 1201.9484 | 1267.68 | 1309.936 | 1341.1085
T50=1 Day α=0.5 | 1014.144 | 1126.8267 | 1267.68 | 1307.1189 | 1330.3825 | 1346.6044
T50=1/2 Day α=0.5 | 1126.8267 | 1216.9728 | 1307.1189 | 1328.8783 | 1341.1085 | 1349.3866

## Slide 18: PILE DRIVING FORMULA
Three formula:
Engineering News (EN)
Modified Gates (MG)
Washington DOT (WSDOT)

## Slide 19: FORMULA COMPARISON
Test No. | Eng. News (EN) kips |  | Modified Gates (MG) kips |  | WSDOT kips | 
 | 5 feet | 1 foot | 5 feet | 1 foot | 5 feet | 1 foot
1 | 1221 | 1424 | 420 | 460 | 286 | 326
2 | 1814 | 1855 | 511 | 517 | 341 | 344
3 | 1354 | 1408 | 443 | 450 | 301 | 303
4 | 1556 | 1420 | 475 | 455 | 322 | 313
5 | 1415 | 1473 | 452 | 461 | 306 | 311
6 | 1579 | 1733 | 477 | 501 | 322 | 339
7 | 1776 | 1863 | 504 | 518 | 330 | 345
8 | 1284 | 1311 | 439 | 446 | 317 | 327
9 | 1429 | 1477 | 464 | 471 | 338 | 342
10 | 2056 | 1974 | 547 | 537 | 363 | 366
11 | 1018 | 1767 | 371 | 499 | 229 | 307
12 | 686 | 871 | 311 | 354 | 211 | 242
13 | 1521 | 1720 | 455 | 490 | 262 | 281
14 | 1063 | 1237 | 393 | 424 | 270 | 290

## Slide 20: FORMULA EVALUATION
Test No. | EN |  | MG |  | WSDOT | 
 | Diff. kips | DRu1/Ru5 | Diff. kips | Ru1/Ru5 | Diff. kips | Ru1/Ru5
1 | -204 | 1.17 | -39 | 1.09 | -39 | 1.14
2 | -41 | 1.02 | -6 | 1.01 | -3 | 1.01
3 | -54 | 1.04 | -8 | 1.02 | -2 | 1.01
4 | 136 | 0.91 | 20 | 0.96 | 9 | 0.97
5 | -58 | 1.04 | -9 | 1.02 | -5 | 1.02
6 | -153 | 1.1 | -24 | 1.05 | -18 | 1.05
7 | -87 | 1.05 | -14 | 1.03 | -14 | 1.04
8 | -27 | 1.02 | -7 | 1.01 | -9 | 1.03
9 | -48 | 1.03 | -7 | 1.02 | -4 | 1.01
10 | 82 | 0.96 | 10 | 0.98 | -3 | 1.01
11 | -748 | 1.73 | -127 | 1.34 | -78 | 1.34
12 | -185 | 1.27 | -43 | 1.14 | -31 | 1.15
13 | -199 | 1.13 | -35 | 1.08 | -19 | 1.07
14 | -174 | 1.16 | -31 | 1.08 | -21 | 1.08
Mean | -125.7 | 1.1 | -22.8 | 1.1 | -17.0 | 1.1
STDEV | 206.0 | 0.2 | 35.0 | 0.1 | 21.7 | 0.1
COV,% | -163.9 | 17.8 | -153.2 | 8.8 | -127.4 | 8.8

## Slide 21
Chart: Nominal Resistance Comparison Estimated Using Bottom 5 feet Driving Data
| 1650 | 2722 | 1868 | 3674 | 2936 | 1824 | 1779 | 1890 | 1459 | 2002 | 1779 | 1059 | 1352 | 1793
EN | 5429 | 8070 | 6024 | 6922 | 6294 | 7025 | 7900 | 5712 | 6357 | 9146 | 4530 | 3051 | 6764 | 4727
Mod. Gates | 1870.261 | 2274.7506 | 1968.7012 | 2111.3156 | 2010.3765 | 2123.3051 | 2242.566 | 1953.6007 | 2063.6758 | 2431.0689 | 1652.49 | 1382.8502 | 2024.5661 | 1747.7871
WSDOT | 1274 | 1517 | 1337 | 1434 | 1360 | 1432 | 1469 | 1412 | 1503 | 1614 | 1017 | 938 | 1167 | 1199
 | 0 | 10000
CAPWAP Restrike | 1499 | 2424 | 1748 | 3505 | 2802 | 1535 | 1686 | 1846 | 1219 | 1953 | 1530 | 1010 | 1210 | 1583
FORMULA COMPARISON cont.

## Slide 22
The MG and WSDOT driving formulae are more accurate than the EN formula in estimating nominal static resistance in west Tennessee. The use of the EN formula should be discontinued.
The average driving data (blow count and hammer drop height) over the bottom 5 feet of driving is appropriate for friction piles in west Tennessee.
The average should be taken over the bottom one foot if a layer of very dense material is present at or above the pile tip elevations.
The Modified Bogard & Matlock equation can be used to provide a fairly accurate estimate of the CAPWAP restrike resistance in west Tennessee using the nominal long-term static resistance, a values of 0.2 to 0.5 and T50 values of ½ to 2 days.
CONCLUSIONS

## Slide 23: PILE INTEGRITY
F = Zv Z = Impedance = EA/c

## Slide 24: PILE INTEGRITY-cont.
F = Zv Z = Impedance = EA/c
When Impedance changes, part of the downward traveling stress wave is reflected up and part continues to travel down
When the cross section of the pile is reduced, the up reflected stress wave is tensile, its magnitude indicates the extent of the cross section change

## Slide 25: PILE INTEGRITY-cont.
PDA calculates a relative integrity factor (b)
When Impedance does not change, b = 1
GRL recommendations (2007):
  b > 0.8  slight damage
  b < 0.6  serious damage

## Slide 26: DETECTING DAMAGED PILES HAMMER MALFUNCTION

## Slide 27
DETECTING DAMAGED PILES POOR SPLICING

## Slide 28: PILE EMBEDMENT
Piles are to penetrate through liquefiable soils into non-liquefying stratum
There were difficulties achieving the design tip elevations at some locations
Need to assess:
  Pile resistance
  Liquefiable zones
  Change in subsurface conditions due to pile driving
Need for reliable, quick subsurface information

## Slide 29: CPT
Chart: Friction Ratio (%)
Chart: Soil Profile
Silty Sand to Sandy Silt | 0.3
Sand to Silty Sand | 0.05
Silty Sand to Sandy Silt | 0.05
Sandy Silt to Clayey Silt | 0.3
Silty Sand to Sandy Silt | 0.15
Sandy Silt to Clayey Silt | 0.1
Clayey Silt to Silty Clay | 0.1
Sand to Silty Sand | 0.05
Silty Sand to Sandy Silt | 0.1
Sandy Silt to Clayey Silt | 0.05
Clayey Silt to Silty Clay | 0.05
Sandy Silt to Clayey Silt | 0.2
Chart: Factor of Safety from qT
Chart: Factor of Safety from Vs
| 0.52418329667651065 | 0.46246342704575438 | 0.26287768390249577 | 0.29483120122054668 | 0.4276912523029644
u0 | 3.4 | 4.4 | 22.5 | 23.5 | 24.5

## Slide 30: CPT
Chart: Friction Ratio (%)
Chart: Soil Profile
Silty Sand to Sandy Silt | 0.3
Sand to Silty Sand | 0.05
Silty Sand to Sandy Silt | 0.05
Sandy Silt to Clayey Silt | 0.3
Silty Sand to Sandy Silt | 0.15
Sandy Silt to Clayey Silt | 0.1
Clayey Silt to Silty Clay | 0.1
Sand to Silty Sand | 0.05
Silty Sand to Sandy Silt | 0.1
Sandy Silt to Clayey Silt | 0.05
Clayey Silt to Silty Clay | 0.05
Sandy Silt to Clayey Silt | 0.2
Chart: Factor of Safety from qT
Chart: Factor of Safety from Vs
| 0.52418329667651065 | 0.46246342704575438 | 0.26287768390249577 | 0.29483120122054668 | 0.4276912523029644
u0 | 3.4 | 4.4 | 22.5 | 23.5 | 24.5

## Slide 31: CPT
Chart: Tip Resistance
Chart: Sleeve Friction
Chart: Pore Pressure
Chart: Friction Ratio (%)
Chart: Shear Wave Velocity
| 221.79912975151979 | 155.47159145794069 | 160.01382502970517 | 163.12948382150677 | 120.18391539721921 | 138.77366938226911 | 143.46046431706023 | 174.6455628708618 | 166.62005281957914 | 188.12725668999403 | 183.0430384456028 | 180.46202919233707 | 183.83911422367078 | 186.63171404370792 | 183.24207910097419 | 208.08866750067025 | 194.72824321335054 | 199.8121405932483 | 200.5602126198784 | 209.0458086967773 | 185.05705159661798 | 181.70330702014016 | 192.19630649381122 | 227.15161208882583 | 297.73174777093897 | 299.87490394101621 | 366.52572575988165 | 392.71702129905901
 | 1.3 | 2.35 | 3.4 | 4.4 | 5.4 | 6.4 | 7.4 | 8.4 | 9.4 | 10.45 | 11.5 | 12.5 | 13.5 | 14.5 | 15.5 | 16.5 | 17.5 | 18.45 | 19.45 | 20.5 | 21.5 | 22.5 | 23.5 | 24.5 | 26.05 | 27.7 | 28.85 | 29.95
 | 0 | 1.8 | 1.8 | 2.9 | 2.9 | 3.9 | 3.9 | 4.9 | 4.9 | 5.9 | 5.9 | 6.9 | 6.9 | 7.9 | 7.9 | 8.9 | 8.9 | 9.9 | 9.9 | 11 | 11 | 12 | 12 | 13 | 13 | 14 | 14 | 15 | 15 | 16 | 16 | 17 | 17 | 18 | 18 | 18.9 | 18.9 | 20 | 20 | 21 | 21 | 22 | 22 | 23 | 23 | 24 | 24 | 25 | 25 | 27.1 | 27.1 | 28.3 | 28.3 | 29.4 | 29.4 | 30.5 | 30.5
Chart: Soil Profile
Silty Sand to Sandy Silt | 0.3
Sand to Silty Sand | 0.05
Silty Sand to Sandy Silt | 0.05
Sandy Silt to Clayey Silt | 0.3
Silty Sand to Sandy Silt | 0.15
Sandy Silt to Clayey Silt | 0.1
Clayey Silt to Silty Clay | 0.1
Sand to Silty Sand | 0.05
Silty Sand to Sandy Silt | 0.1
Sandy Silt to Clayey Silt | 0.05
Clayey Silt to Silty Clay | 0.05
Sandy Silt to Clayey Silt | 0.2
Chart: Factor of Safety from qT
Chart: Factor of Safety from Vs
| 0.52418329667651065 | 0.46246342704575438 | 0.26287768390249577 | 0.29483120122054668 | 0.4276912523029644
u0 | 3.4 | 4.4 | 22.5 | 23.5 | 24.5

## Slide 32: CPT AREAS OF STUDY
Notes: This is an overhead view showing the site location along Summer Ave.

## Slide 33: SUPPLEMENTAL LIQUEFACTION STUDY

## Slide 34: IMPACT OF PILE DRIVING

## Slide 35
Top of non-liquefiable zone
Pile tip (original)
Pile tip (new)
Bottom of cap
Ground surface
CPT-3
CPT-4
I-40/240 Bridge 2, Bent 5
Liquefiable zone from SPT boring
Liquefiable zone from SPT boring
Liquefaction FOS Plot
Liquefaction FOS Plot
SUPPLEMENTAL LIQUEFACTION STUDY

## Slide 36: WALLS 17 AND 19
Wall 17
Wall 19

## Slide 37
CPT-3
CPT-4
CPT-7
MIN. PILE TIP El. 203.75
(per plans)
PILE TIP EL. 211.00
(proposed)
PILE CUTOFF EL. 243.89
Liquefiable zone
CPT-8
WALL NO. 19
CONE REFUSAL @ 35 feet
CONE REFUSAL @ 56 feet
Boring from ‘07

## Slide 38: WALLS 15 &16

## Slide 39: WALL 21
Problem: Insufficient factors of safety against global instability in seismic conditions
Solution: Ground improvement using rammed aggregate piers

## Slide 40: WALL 21

## Slide 41: WALL 10
Needed to widen I-40 WB ramp
Two approved wall types
  Soldier Pile (embedded in drilled shafts) & Lagging Wall
  Pile-supported Cantilever Wall
TDOT set maximum deflection (6 inches for soldier pile wall and 2 inches for CIP wall)
To reduce lateral pressure, EPS foam blocks & light-weight flowable fill are to be used for backfill

## Slide 42: WALL 10

## Slide 43: WALL 10 CHALLENGE

## Slide 44: WALL 10 CHALLENGE cont.
Global stability minimum factors of safety have to be satisfied:
  1.30 static
  1.1 seismic
Initial design utilized soldier pile wall
Procedure:
  Determine the required force per pile (based on wall configuration and pile spacing) to achieve a FoS of 1.10
  Perform LPILE analysis (Chapter 10 Duncan & Wright) to determine min. shaft embedment below failure surface, bending moment and lateral deflection

## Slide 45: WALL 10

## Slide 46: WALL 10

## Slide 47: LPILE ANALYSIS
Location of Slip Surface

## Slide 48: WALL 10
Two or three Pile Rows
Geofoam

## Slide 49: WALL 10 – GROUP ANALYSIS

## Slide 50
WALL 10 CONSTRUCTION

## Slide 51
WALL 10 CONSTRUCTION

## Slide 52
PROJECT PROGRESS (JUNE 2015)

## Slide 54
BRIDGE 2

## Slide 55
BRIDGE 1

## Slide 56
PROJECT PROGRESS (August, 2016)