## Slide 1
Monitoring of Retaining Wall Lateral Earth Pressures Within High Plasticity, Expansive (Yazoo) Clay

## Slide 2: SITE PLAN AND GENERALIZED SOIL PROFILE

## Slide 3: RETAINING WALL BORING LOGS
BORING B-1
BORING B-2

## Slide 4
TYPICAL RETAINING WALL BORING

## Slide 5: RETAINING WALL BORING LOGS
SUMMARY SOIL PROPERTIES
WEATHERED YAZOO CLAY
Ɣ = 111 PCF
C = 2,100 PSF
ᶲ = 0°
WATER CONTENT – 33% TO 48%
LIQUID LIMIT – 100% TO 113%
PI – 72% TO 75%
UNWEATHERED YAZOO CLAY
Ɣ = 114 PCF
C = 6,600 PSF
ᶲ = 0°
WATER CONTENT - 28% TO 44%
LIQUID LIMIT – 92% TO 107%
PI – 59% TO 69%
BORING B-3

## Slide 6: EXTENT OF YAZOO CLAY WITHIN THREE STATE AREA
Ref.: Lee Jr., Landis T., “State Study 151 and 236: Yazoo Clay
Investigation; USACE ERDC; June 2012.

## Slide 7: ASSUMED TO ORIGINATE IN THE EOCENE ERA JACKSON GROUP, YAZOO FORMATION JACKSON DOME, 25 SQ. MILES CENTERED APPROX. 2000 FEET BELOW JACKSON DIPS IN ALL DIRECTIONS FROM DOME YAZOO CLAY OUTCROPS IN 6 COUNTIES IN MISSISSIPPI
Ref.: Lee Jr., Landis T., “State Study 151 and 236: Yazoo Clay
Investigation; USACE ERDC; June 2012.

## Slide 8: GEOLOGIC VICINITY AND SITE LOCATION
SITE LOCATION
Ref.: Lee Jr., Landis T., “State Study 151 and 236: Yazoo Clay
Investigation; USACE ERDC; June 2012.

## Slide 9: YAZOO CLAY
BEIGE, YELLOWISH ORANGE (OXIDIZED/WEATHERED), HIGH PLASTICITY, MONTMORILLIC CLAY (CH); CAN BE CALCAREOUS AND CONTAIN GYPSUM
BLUE-GRAY, UNWEATHERED, CALCAREOUS, FOSSILIFEROUS, SLIGHTLY SILTY, HIGH PLASTICITY, MONTMORILLIC CLAY (CH); TRACE THIN LIMESTONES AND BENTOTONIC CLAY

## Slide 10: CONSTRUCTION PLAN, PROFILE & SECTION

## Slide 11: SHAFTS 62, 64 AND 76

## Slide 12: DESIGN LATERAL EARTH PRESSURES
DESIGN LATERAL EARTH PRESSURES IN HIGHLY PLASTIC, EXPANSIVE, WEATHERED YAZZO CLAY CONSIDERING SWELLING POTENITAL OF THESE SOILS.
DR. LYTTON’S EXPANSIVE LATERAL EARTH PRESSURE THEORY USED TO ESTIMATE LATERAL EARTH PRESSURES IN THE SOIL IN THE UPPER FIVE FEET.
ZONE 1 (0 FEET TO 5 FEET) – MAXIMUM LATERAL EARTH PRESSURE ESTIMATED TO BE EQUAL TO THE PASSIVE EARTH PRESSURE ASSUMING UNDRAINED SHEAR STRENGTH OF 2,000 PSF.
ZONE 2 (BETWEEN 5 FEET AND 12 FEET) – LATERAL EARTH PRESSURE TO VARY LINEARLY BETWEEN THE BOTTOM OF ZONE 1 AND THE TOP OF ZONE 3.
ZONE 3 (SOIL DEPTH GREATER THAN 12 FEET) – MAXIMUM LATERAL EARTH PRESSURE ESTIMATED TO EQUAL THE AT-REST EARTH PRESSURES.

## Slide 13
Ref.: Burns Cooley Dennis, Inc., “Geotechnical Investigation, I-55 Reconstruction Near Steed Road, Paul Moak GMC Retaining Wall, Madison County, MS; Report No. 060295-1; June 23, 2008.

## Slide 14: TOP OF WALL MODIFICATIONS

## Slide 15
Ref.: Burns Cooley Dennis, Inc., “Geotechnical Investigation, I-55 Reconstruction Near Steed Road, Paul Moak GMC Retaining Wall, Madison County, MS; Report No. 060295-1; June 23, 2008.

## Slide 16: INSTRUMENTATION DIAGRAM

## Slide 17: SHAFT 62

## Slide 18: SHAFT 62 CONTINUED

## Slide 19: SHAFT 62 ABANDONED

## Slide 20: SHAFT 64

## Slide 21: SHAFT 64
WATER CONTENT = 44% PI = 60% LIQUID LIMIT = 91% VOLUME CHANGE = 163%
WATER CONTENT = 36% PI = 51% LIQUID LIMIT = 78% VOLUME CHANGE = 130%
WEATHERED YAZOO CLAY
UNWEATHERED YAZOO CLAY

## Slide 22: SHAFT 76

## Slide 23: SHAFT 76
WATER CONTENT = 46% PI = 65% LIQUID LIMIT = 99% VOLUME CHANGE = 184%
WATER CONTENT =40% PI = 52% LIQUID LIMIT =81% VOLUME CHANGE = 136%
WEATHERED YAZOO CLAY
UNWEATHERED YAZOO CLAY

## Slide 24: BASELINE READINGS AND SOIL BACKFILL
(AUG. 15, 2102)

## Slide 25: SHAFT EXCAVATION (Sept. 12, 2012)
SHAFT 64
SHAFT 64

## Slide 26: SHAFT EXCAVATION (Sept. 12, 2012)
SHAFT 76
SHAFT 64
SHAFT 76

## Slide 27: Shaft 76 Inclinometer

## Slide 28: WALL PANEL CONSTRUCTION
(April 10, 2013)

## Slide 29: WALL CONSTRUCTION (June 23, 2013)
SHAFT 76
SHAFT 64

## Slide 41: COMPLETED WALL (August 2103)